FMI - HOT WORK PERMIT

A HOT WORK PERMIT IS REQUIRED FOR ANY TEMPORARY OPERATION INVOLVING OPEN FLAMES, PRODUCING HEAT &/OR SPARKS.

Note:  Hot work permits are not required in designated welding/cutting locations such as welding booths designed to eliminate hazards w/ proper safeguards in place.

| Permit Requested by | Permit # | Date |
| --- | --- | --- |
| Plant or Location | Unit | Floor/Other location/Equipment |

HOT WORK OF ANY TYPE IS PROHIBITED NEAR OPERATING COMBUSTION TURBINES FUEL SYSTEMS OR IN FUEL HANDLING AREAS WHEN CONVEYORS ARE OPERATING.

| Type of work being conducted: | Arc Welding ( ) | TIG/MIG Welding ( ) | Oxy-Fuel Cutting ( ) | Plasma Cutting ( ) | Brazing ( ) | Soldering ( ) | Heating ( ) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Other type of heat source or special conditions: |  |  |  |  |  |  |  |

PRECAUTIONS

Assessment of the work area must be performed							 YES		NO	     N/A

| Ensure that the immediate work area is properly maintained and floor is swept clean of combustible /flammable material. |  |  |  |
| --- | --- | --- | --- |
| Relocate portable combustible/flammable material at least 35 feet from the point of operation. |  |  |  |
| Protect stationary combustible /flammable material within a 35-ft radius from the heat/spark generated at the point of operation. |  |  |  |
| Protect wall/floor openings, ventilation ducts, drains, and conveyor systems from heat/spark generated at the point of operation. |  |  |  |
| If applicable, check for explosive vapors within the immediate work area with a confined space monitoring meter. |  |  |  |
| De-energize equipment that could produce a hazardous environment during hot work applications. |  |  |  |
| Confirm that the fire protection systems are functional and an appropriate portable fire extinguisher is at the work site. |  |  |  |
| Confirm that adequate personnel assigned to the hot work have had fire safety including training in use of portable fire extinguisher. Area must have a fire watch during and for a minimum of 30 minutes after hot work is completed. |  |  |  |
| Install warning devices (i.e., signs, ropes, etc.) to protect other employees within the area. |  |  |  |
| Install barriers, fire blankets, and/or screens to protect other employees from eye injuries. |  |  |  |
| Determine that the cutting/welding equipment is in good repair. |  |  |  |

| Estimated Start Date | Time |  | Estimated End Date |  | Time |
| --- | --- | --- | --- | --- | --- |
| The location where work is to be done has been inspected and all necessary precautions have been completed. |  |  | Verified by permit holder (Employee/Contractor) Signature: |  |  |
| A designated fire watch has been assigned |  | Printed Name: |  | Signature: |  |

HOT WORK PERMIT – AUTHORIZATION (Operating Authority/Lead Employee on Site / Contract Administrator)

| Permission has been granted for this work | Signature |  | Date | Time |
| --- | --- | --- | --- | --- |
| Hot work permit area tag prepared Yes ( ) No ( ) |  | Tag # | Hot work area caution sign provided Yes ( ) No ( ) |  |

HOT WORK COMPLETION  - PERMIT RELEASE

If any of the questions below are Yes, the work requires a hot work permit.

| Has the work area and all adjacent areas to which sparks and heat might have been spread (i.e., adjacent walls, floor/wall openings, conveyor systems, etc.) been inspected 30 minutes after the work was completed and were they found safe? |  |  | Yes ( ) No ( ) |  |
| --- | --- | --- | --- | --- |
| Were the fire extinguishers and any other portable fire equipment used returned to the proper storage area? If fire extinguishers were used they must be replaced with fully charged units. |  |  | Yes ( ) No ( ) |  |
| Hot Work is complete and post 30 minute Fire Watch confirmed area is clear of fire hazard. | Signature of assigned fire watch | Date |  | Time |
| Hot Work is complete and Operating Authority/Lead Employee/Contract Administrator on site has been notified | Signature of permit holder (employee/contractor) | Date |  | Time |

Closed hot work permits shall be retained for 90 days by the operating authority